## COAL and NG calcs
origin | Gerdes, K. J. (2013). Cost and Performance Comparison Baseline for Fossil Energy Power Plants, 1–626.
[10 empty] | Normalized coal flow rate | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
[10 empty] | Factor | 1.0709 | 1.0267 | 1.0871 | 1.0326 | 1.1451 | 1.0747 | 1.1432 | 0.81302 | 1.2209 | 0.88367
[7 empty] | Share | 0.6 | 0.4 | Operations and Maintenance | 4%
[7 empty] | TJ/million | 6.23 | 5.76 | Economic energy intensity | 5.4855 | TJ/$million 2007 |  | 1.5237 | GWh/$million
[7 empty] | PPI | 2002 | 2007 | Lifetime | 30 | years
[8 empty] | 138 | 152 | Capacity factor | 85%
[10 empty] | EROIfuel | Coal | 58 | Gas | 58
[11 empty] | Exhibit 3-101 pg 297 | [5 empty] | Exhibit 4-58 pg 436 |  |  |  | Exhibit 5-27 pg. 499
[11 empty] | Coal Integrated Gasification Combined Cycle | [5 empty] | Pulverized Coal |  |  |  | Natural Gas Combined Cycle
IGCC | Exhibit 3-101 pg 297 | [8 empty] | Case number | 1 | 2 (CCS) | 3 | 4 (CCS) | 5 | 6 (CCS) | 9 | 10 (CCS) | 11 | 12 (CCS) | 13 | 14 (CCS)
[10 empty] | Fuel Flowrate (lb/hr) | 466901 | 487011 | 459958 | 484212 | 436646 | 465264 | 437378 | 614994 | 409528 | 565820 | 167333 | 167333
|  | Integrated Gasification Combined Cycle | [7 empty] | Gross Power Output (kWe) | 747800 | 734000 | 738200 | 703700 | 737000 | 673400 | 582600 | 672700 | 580400 | 662800 | 564700 | 511000
[10 empty] | Auxiliary Power Requirement (kWe) | 125750 | 190750 | 113140 | 190090 | 108020 | 176540 | 32580 | 122740 | 30410 | 112830 | 9620 | 37430
|  | GEE R+Q |  | CoP E-Gas FSQ |  | Shell |  |  |  | Net Power Output (kWe) | 622050 | 543250 | 625060 | 513610 | 628980 | 496860 | 550020 | 549960 | 549990 | 549970 | 555080 | 473570
[10 empty] | Net Plant HHV Efficiency (%) | 39% | 32.6% | 39.7% | 31% | 42.1% | 31.2% | 36.8% | 26.2% | 39.3% | 28.4% | 50.2% | 42.8%
[10 empty] | Total Plant Overnight Cost (2007$/kW) | 1987 | 2711 | 1913 | 2817 | 2217 | 3181 | 1622 | 2942 | 1647 | 2913 | 584 | 1226
| PERFORMANCE | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 |  |  | Data source NETL | Exhibit 3-101 | [5 empty] | Exhibit 4-58 |  |  |  | Exhibit 5-27
[11 empty] | Normalized for coal flowrate =500000 lb/hr | [5 empty] | Normalized for coal flowrate =500000 lb/hr
[10 empty] | Fuel Input (kWth) | 1708070.8758 | 1710855.651 | 1711524.1373 | 1710827.5421 | 1710784.3102 | 1711393.9613 | 1708613.1049 | 1706588.9825 | 1708632.4364 | 1711245.7005 | 1105737.0518 | 1106471.9626
[10 empty] | Gross Efficiency | 46.88% | 44.05% | 46.89% | 42.47% | 49.33% | 42.29% | 38.98% | 32.05% | 41.47% | 34.23% | 51.07% | 46.18%
| CO2 Capture | 0% | 90% | 0% | 90% | 0% | 90% |  |  | Gross Power Output (kWe) | 800812.1636 | 753576.4079 | 802464.5729 | 726644.5276 | 843933.0716 | 723675.1608 | 666014.2943 | 546915.9049 | 708620.656 | 585698.6321 | 564700 | 511000
[10 empty] | Auxiliary Power Requirement (kWe) | 134664.522 | 195837.4657 | 122989.4903 | 196287.9896 | 123692.8771 | 189720.2449 | 37244.6717 | 99789.5914 | 37128.1085 | 99704.8531 | 9620 | 37430
| Gross Power Output (kWe) | 747800 | 734000 | 738200 | 703700 | 737000 | 673400 |  |  | Net Power Output (kWe) | 666147.6416 | 557738.9422 | 679475.0825 | 530356.538 | 720240.1946 | 533954.9159 | 628769.6226 | 447126.3134 | 671492.5475 | 485993.7789 | 555080 | 473570
| Auxiliary Power Requirement (kWe) | [8 empty] | Gross power difference |  | 47235.7557 |  | 75820.0452 |  | 120257.9109 |  | 119098.3894 |  | 122922.0239 |  | 53700
[10 empty] | Aux Power Difference |  | 61172.9437 |  | 73298.4992 |  | 66027.3678 |  | 62544.9198 |  | 62576.7447 |  | 27810
[10 empty] | Net Power Difference |  | 108408.6993 |  | 149118.5445 |  | 186285.2787 |  | 181643.3092 |  | 185498.7686 |  | 81510
[10 empty] | Plant Construction Costs ($million) | 1591.2138 | 2042.9456 | 1535.1147 | 2046.9576 | 1870.9996 | 2302.0107 | 1080.2752 | 1609.0266 | 1167.0982 | 1706.1401 | 329.7848 | 626.486
[10 empty] | Eout net (GWh) | 148804.0602 | 124587.7249 | 151781.1439 | 118471.0435 | 160887.2547 | 119274.8491 | 140454.5583 | 99879.0759 | 149998.0053 | 108561.2903 | 123993.7704 | 105786.0666
[10 empty] | Eout (GWh) | 178885.4211 | 168333.898 | 179254.5363 | 162317.8546 | 188517.7695 | 161654.5574 | 148774.2731 | 122170.0748 | 158291.6821 | 130833.3604 | 126142.686 | 114147.18
[10 empty] | Eccs (GWh) |  | 688.3264 |  | 779.9206 |  | 656.7531 |  | 805.685 |  | 821.3651 |  | 452.0985
[10 empty] | Ecap (GWh) | 2424.612 | 2424.612 | 2339.1311 | 2339.1311 | 2850.9357 | 2850.9357 | 1646.0693 | 1646.0693 | 1778.3659 | 1778.3659 | 502.5096 | 502.5096
[10 empty] | Eop = Eaux+Eo&m+Efp (GWh) | 40899.1809 | 41725.1727 | 38065.2248 | 39001.1296 | 38772.0804 | 39560.1841 | 17265.3068 | 18232.1288 | 17372.1611 | 18357.7992 | 7084.3452 | 7626.8634
[10 empty] | Ered (GWh |  | 10551.5231 |  | 16936.6817 |  | 26863.2121 |  | 26604.1982 |  | 27458.3217 |  | 11995.506
[10 empty] | EROIfuel | 58 |  | 58 |  | 58 |  | 58 |  | 58 |  | 58
[10 empty] | EROIel | 4.129 | 3.0391 | 4.4365 | 2.7485 | 4.5292 | 2.3116 | 7.8669 | 2.5835 | 8.2657 | 2.7023 | 16.6265 | 5.5473
[10 empty] | EROI CCS complete |  | 2.4468 |  | 2.2266 |  | 2.071 |  | 2.3744 |  | 2.4865 |  | 4.7544
[10 empty] | EROI Net | 11.2369 | 8.4428 | 11.7378 | 8.0885 | 11.4981 | 7.7264 | 13.2609 | 8.0781 | 13.816 | 8.5725 | 22.8016 | 16.4454
[10 empty] | R and EROI CCS | 1.4826 | 8.4428 | 1.5128 | 8.0885 | 1.2309 | 7.7264 | 1.9248 | 8.0781 | 1.775 | 8.5725 | 3.9189 | 16.4454
| Net Power Output (kWe) | 125750 | 190750 | 113140 | 190090 | 108020 | 176540 |  |  | fop (only plant losses) |  | 16.27% |  | 21.95% |  | 25.86% |  | 28.89% |  | 27.62% |  | 14.68%
| Coal Flowrate (lb/hr) | [8 empty] | fcap (only plant) |  | 28.39% |  | 33.34% |  | 23.04% |  | 48.95% |  | 46.19% |  | 89.97%
[10 empty] | R | 4 | 28.39%
[10 empty] | Eaux | 30081.3609 | 24216.3353 | 27473.3924 | 33310.1005 | 27630.5149 | 42379.7083 | 8319.7148 | 22290.9989 | 8293.6769 | 22272.0701 | 2148.9156 | 8361.1134
[10 empty] | Eom | 2909.5344 | 3735.5261 | 2806.9573 | 3742.862 | 3421.1228 | 4209.2265 | 1975.2832 | 2942.1051 | 2134.0391 | 3119.6772 | 603.0115 | 1145.5297
[10 empty] | Efp | 7908.2856 | 7908.2856 | 7784.8752 | 7784.8752 | 7720.4427 | 7720.4427 | 6970.3089 | 6970.3089 | 6944.4451 | 6944.4451 | 4332.4181 | 4332.4181
[10 empty] | R | 1.4826 | -100% | 1.5128 | -100% | 1.2309 | -100% | 1.9248 | -100% | 1.775 | -100% | 3.9189 | -100%
[10 empty] | Aux power difference |  | 61172.9437 |  | 73298.4992 |  | 66027.3678 |  | 62544.9198 |  | 62576.7447 |  | 27810
[10 empty] | Net power difference | 108408.6993 |  | 149118.5445 |  | 186285.2787 |  | 181643.3092 |  | 185498.7686 |  | 81510
108408.6993
[10 empty] | Auxiliary rates | 16.82% | 25.99% | 15.33% | 27.01% | 14.66% | 26.22% | 5.592% | 18.25% | 5.239% | 17.02% | 1.704% | 7.325%
[10 empty] | Ecap rates | 1.355% | 1.44% | 1.305% | 1.441% | 1.512% | 1.764% | 1.106% | 1.347% | 1.123% | 1.359% | 0.3984% | 0.4402%
EO&M
Eop rates
| Natural Gas Flowrate (lb/hr) | 622050 | 543250 | 625060 | 513610 | 628980 | 496860
HHV Thermal Input (kWth)
| Net Plant HHV Efficiency (%) | 466901 | 487011 | 459958 | 484212 | 436646 | 465264
Net Plant HHV Heat Rate (Btu/kWh)
|  | N/A | N/A | N/A | N/A | N/A | N/A
|  | 1596320 | 1665074 | 1572582 | 1655503 | 1492878 | 1590722
|  | 39% | 32.6% | 39.7% | 31% | 42.1% | 31.2%
|  | 8756 | 10458 | 8585 | 10998 | 8099 | 10924
| Raw Water Withdrawal (gpm/MWnet) Process Water Discharge (gpm/MWnet) Raw Water Consumption (gpm/MWnet) | 7.6 | 10.7 | 7 | 11.1 | 6.6 | 11.3
|  | 1.6 | 2 | 1.4 | 2.1 | 1.2 | 2
|  | 6 | 8.7 | 5.5 | 9 | 5.3 | 9.3
| CO2 Emissions (lb/MMBtu) CO2 Emissions (lb/MWhgross) CO2 Emissions (lb/MWhnet) SO2 Emissions (lb/MMBtu) SO2 Emissions (lb/MWhgross) NOx Emissions (lb/MMBtu) NOx Emissions (lb/MWhgross) PM Emissions (lb/MMBtu) PM Emissions (lb/MWhgross) | 197 | 20 | 199 | 20 | 197 | 20
| Hg Emissions (lb/TBtu) | 1434 | 152 | 1448 | 158 | 1361 | 161
Hg Emissions (lb/MWhgross)
|  | 1723 | 206 | 1710 | 217 | 1595 | 218
|  | 0.0012 | 0.0022 | 0.0117 | 0.0022 | 0.0042 | 0.0021
|  | 0.009 | 0.0166 | 0.0852 | 0.0173 | 0.029 | 0.0171
|  | 0.059 | 0.049 | 0.06 | 0.049 | 0.059 | 0.049
|  | 0.43 | 0.376 | 0.434 | 0.396 | 0.409 | 0.396
|  | 0.0071 | 0.0071 | 0.0071 | 0.0071 | 0.0071 | 0.0071
|  | 0.052 | 0.055 | 0.052 | 0.057 | 0.049 | 0.057
|  | 0.571 | 0.571 | 0.571 | 0.571 | 0.571 | 0.571
|  | 4.16e-06 | 4.42e-06 | 4.15e-06 | 4.59e-06 | 3.95e-06 | 4.61e-06
COST
| Total Plant Cost (2007$/kW) Total Overnight Cost (2007$/kW) | 1987 | 2711 | 1913 | 2817 | 2217 | 3181
| Bare Erected Cost Home Office Expenses Project Contingency Process Contingency Owner'sCosts | 2447 | 3334 | 2351 | 3466 | 2716 | 3904
| Total Overnight Cost (2007$ x 1,000) Total As Spent Capital (2007$/kW) COE (mills/kWh, 2007$)1,2 | 1528 | 2032 | 1470 | 2113 | 1695 | 2385
| CO2 TS&M Costs Fuel Costs Variable Costs Fixed Costs Capital Costs | 144 | 191 | 138 | 199 | 156 | 221
| LCOE (mills/kWh, 2007$)1,2 | 265 | 369 | 256 | 385 | 302 | 444
|  | 50 | 119 | 50 | 120 | 63 | 131
|  | 460 | 623 | 438 | 649 | 500 | 723
|  | 1521880 | 1811411 | 1469577 | 1780290 | 1708524 | 1939878
|  | 2789 | 3801 | 2680 | 3952 | 3097 | 4451
|  | 76.3 | 105.6 | 74 | 110.3 | 81.3 | 119.4
|  | 0 | 5.2 | 0 | 5.5 | 0 | 5.6
|  | 14.3 | 17.1 | 14 | 18 | 13.3 | 17.9
|  | 7.3 | 9.3 | 7.2 | 9.8 | 7.8 | 9.9
|  | 11.3 | 14.8 | 11.1 | 15.5 | 12.1 | 16.7
|  | 43.4 | 59.1 | 41.7 | 61.5 | 48.2 | 69.2
|  | 96.7 | 133.9 | 93.8 | 139.9 | 103.1 | 151.4
PC | Exhibit 4-58 pg 436
Pulverized Coal Boiler
|  | PC Subcritical |  | PC Supercritical
| PERFORMANCE | Case 9 | Case 10 | Case 11 | Case 12
| CO2 Capture | 0% | 90% | 0% | 90%
| Gross Power Output (kWe) | 582600 | 672700 | 580400 | 662800
Auxiliary Power Requirement (kWe) Net Power Output (kWe)
| Coal Flowrate (lb/hr) | 32580 | 122740 | 30410 | 112830
Natural Gas Flowrate (lb/hr)
| HHV Thermal Input (kWth) | 550020 | 549960 | 549990 | 549970
Net Plant HHV Efficiency (%)
| Net Plant HHV Heat Rate (Btu/kWh) | 437378 | 614994 | 409528 | 565820
|  | N/A | N/A | N/A | N/A
|  | 1495379 | 2102643 | 1400162 | 1934519
|  | 36.8% | 26.2% | 39.3% | 28.4%
|  | 9277 | 13046 | 8687 | 12002
| Raw Water Withdrawal (gpm/MWnet) Process Water Discharge (gpm/MWnet) Raw Water Consumption (gpm/MWnet) | 10.7 | 20.4 | 9.7 | 18.3
|  | 2.2 | 4.7 | 2 | 4.3
|  | 8.5 | 15.7 | 7.7 | 14.1
| CO2 Emissions (lb/MMBtu) CO2 Emissions (lb/MWhgross) CO2 Emissions (lb/MWhnet) SO2 Emissions (lb/MMBtu) SO2 Emissions (lb/MWhgross) NOx Emissions (lb/MMBtu) NOx Emissions (lb/MWhgross) PM Emissions (lb/MMBtu) PM Emissions (lb/MWhgross) | 204 | 20 | 204 | 20
| Hg Emissions (lb/TBtu) | 1783 | 217 | 1675 | 203
Hg Emissions (lb/MWhgross)
|  | 1888 | 266 | 1768 | 244
|  | 0.0858 | 0.0017 | 0.0858 | 0.0016
|  | 0.7515 | 0.0176 | 0.7063 | 0.0162
|  | 0.07 | 0.07 | 0.07 | 0.07
|  | 0.613 | 0.747 | 0.576 | 0.697
|  | 0.013 | 0.013 | 0.013 | 0.013
|  | 0.114 | 0.139 | 0.107 | 0.129
|  | 1.143 | 1.143 | 1.143 | 1.143
|  | 1e-05 | 1.22e-05 | 9.41e-06 | 1.14e-05
COST | bar: Case 1 to Case 4
| Total Plant Cost (2007$/kW) Total Overnight Cost (2007$/kW) | 1622 | 2942 | 1647 | 2913
| Bare Erected Cost Home Office Expenses Project Contingency Process Contingency Owner'sCosts | 1996 | 3610 | 2024 | 3570
| Total Overnight Cost (2007$ x 1,000) Total As Spent Capital (2007$/kW) COE (mills/kWh, 2007$)1,2 | 1317 | 2255 | 1345 | 2239
| CO2 TS&M Costs Fuel Costs Variable Costs Fixed Costs Capital Costs | 124 | 213 | 127 | 211
| LCOE (mills/kWh, 2007$)1,2 | 182 | 369 | 176 | 362
|  | 0 | 105 | 0 | 100
|  | 374 | 667 | 377 | 657
|  | 1098124 | 1985432 | 1113445 | 1963644
|  | 2264 | 4115 | 2296 | 4070
|  | 59.4 | 109.6 | 58.9 | 106.5
|  | 0 | 5.8 | 0 | 5.6
|  | 15.2 | 21.3 | 14.2 | 19.6
|  | 5.1 | 9.2 | 5 | 8.7
|  | 7.8 | 13.1 | 8 | 13
|  | 31.2 | 60.2 | 31.7 | 59.6
|  | 75.3 | 139 | 74.7 | 135.2
NGCC | Exhibit 5-27 pg. 499
NGCC
Advanced F Class
| PERFORMANCE | Case 1: Case 13; Case 2: Case 14
| CO2 Capture | Case 1: 0%; Case 2: 90%
| Gross Power Output (kWe) | Case 1: 564700; Case 2: 511000
Auxiliary Power Requirement (kWe) Net Power Output (kWe)
| Coal Flowrate (lb/hr) | Case 1: 9620; Case 2: 37430
Natural Gas Flowrate (lb/hr)
| HHV Thermal Input (kWth) | Case 1: 555080; Case 2: 473570
Net Plant HHV Efficiency (%)
| Net Plant HHV Heat Rate (Btu/kWh) | Case 1: N/A; Case 2: N/A
|  | 167333 | 167333
|  | 1105812 | 1105812
|  | 50.2% | 42.8%
|  | 6798 | 7968
| Raw Water Withdrawal (gpm/MWnet) Process Water Discharge (gpm/MWnet) Raw Water Consumption (gpm/MWnet) | Case 1: 4.3; Case 2: 8.4
|  | 1 | 2.1
|  | 3.3 | 6.3
| CO2 Emissions (lb/MMBtu) CO2 Emissions (lb/MWhgross) CO2 Emissions (lb/MWhnet) SO2 Emissions (lb/MMBtu) SO2 Emissions (lb/MWhgross) NOx Emissions (lb/MMBtu) NOx Emissions (lb/MWhgross) PM Emissions (lb/MMBtu) PM Emissions (lb/MWhgross) | Case 1: 118; Case 2: 12
| Hg Emissions (lb/TBtu) | Case 1: 790; Case 2: 87
Hg Emissions (lb/MWhgross)
|  | 804 | 94
|  | Negligible | Negligible
|  | Negligible | Negligible
|  | 0.009 | 0.008
|  | 0.06 | 0.061
|  | Negligible | Negligible
|  | Negligible | Negligible
|  | Negligible | Negligible
|  | Negligible | Negligible
COST | bar: Case 1 to Case 2
| Total Plant Cost (2007$/kW) Total Overnight Cost (2007$/kW) | Case 1: 584; Case 2: 1226
| Bare Erected Cost Home Office Expenses Project Contingency Process Contingency Owner'sCosts | Case 1: 718; Case 2: 1497
| Total Overnight Cost (2007$ x 1,000) Total As Spent Capital (2007$/kW) COE (mills/kWh, 2007$)1,2 | Case 1: 482; Case 2: 926
| CO2 TS&M Costs Fuel Costs Variable Costs Fixed Costs Capital Costs | Case 1: 40; Case 2: 78
| LCOE (mills/kWh, 2007$)1,2 | Case 1: 62; Case 2: 162
|  | 0 | 60
|  | 133 | 271
|  | 398290 | 709039
|  | 771 | 1614
|  | 58.9 | 85.9
|  | 0 | 3.2
|  | 44.5 | 52.2
|  | 1.3 | 2.6
|  | 3 | 5.7
|  | 10.1 | 22.3
|  | 74.7 | 108.9